# OPC Server Consolidation — Device Compatibility Assessment

Prepared by: Blue Ridge Automation · For: Madison Precision Products · Date: 2026-08-12 Subject: Can the new MES reach all plant-floor devices through Ignition’s built-in OPC-UA server, allowing TOP Server and OmniServer to be removed?

## 1. Purpose

The new MES (Ignition) currently reaches shop-floor devices through two third-party OPC servers:

- TOP Server (Software Toolbox) — the PLCs and HMIs (assembly cells, vision cells, container/sort stations).

- OmniServer (Software Toolbox) — the weigh-check scales.

MPP has asked whether both can be eliminated by having Ignition talk to the devices directly through its built-in OPC-UA server and drivers. This document states which devices can move to Ignition natively, which cannot, what information we need from MPP, and our recommendation.

Key point up front: “Ignition’s built-in OPC-UA server” is really a question of device drivers — Ignition’s OPC-UA server publishes whatever its drivers can connect to. So the question is whether Ignition’s native driver set covers each device.

## 2. Bottom line

- Most of the automation moves natively. The 9 Allen-Bradley MicroLogix 1400 PLCs (vision, tray disposition, sort) are directly supported by Ignition’s native Allen-Bradley driver — no third-party server needed for these.

- 11 devices cannot be brought into Ignition natively: the 7 weigh scales (custom serial protocol) and the 4 Pro-face LT3300 HMI cells (no Ignition driver).

- 2 devices need a quick confirmation — the 5G0 serialized cells (generic EtherNet/IP).

- Because of the scales and the Pro-face HMIs, a “pure Ignition, zero third-party OPC server” outcome is not achievable without custom development. The cleaner path is to consolidate the two servers into one (Section 5).

## 3. Devices that MOVE to Ignition natively (good news)

Allen-Bradley MicroLogix 1400 — Ignition’s native AB driver speaks EtherNet/IP with the same data-file addressing these PLCs already use:

| Device | Line / station |
| --- | --- |
| 5J6_OilPan, 5K8_64A_OilPan, 6C2_6MA_OilPan | Vision inspection cells |
| 6B2_CH, 6FB_CH, 6MA_CH, RPY_CH | Container / tray-disposition |
| Sort_OilPan, Sort_Totes | Sort cage |

No OPC server needed for these — they connect straight to Ignition.

## 4. Devices that CANNOT be brought into Ignition natively

### 4a. Weigh scales — currently on OmniServer (7 devices)

| Device | Line / station |
| --- | --- |
| 59B_1_FP_1 | 59B Cam Holder — Fuel Pump scale |
| 5PA_1_FP_1 | 5PA Fuel Pump scale |
| 6B2_1_FP_1 | RPY 6B2 Line 2 scale |
| RPY_1_FP_1 | Fuel Pump (RPY 66V) scale |
| RPY_1_CB_1 | RPY Comp Bracket scale |
| 5G0_Front_Scale | 5G0 Front assembly scale |
| 5G0_Rear_Scale | 5G0 Rear assembly scale |

Why not: these use a custom serial/ASCII protocol (OmniServer’s specialty). Ignition has no generic scale or custom-protocol driver. In addition, the target-vs-tolerance pass/fail decision is computed in the OmniServer protocol layer today — the MES reads a “target met” flag rather than calculating it — so that logic would also have to be reproduced.

### 4b. Pro-face LT3300 HMI cells — currently on TOP Server (4 devices)

| Device | Line / station |
| --- | --- |
| 5A2_L1_CamHolder | 5A2 Line 1 — Cam Holder assembly |
| 5A2_L1_FuelPump | 5A2 Line 1 — Fuel Pump assembly |
| 5A2_L2_CamHolder | 5A2 Line 2 — Cam Holder assembly |
| 5A2_L2_FuelPump | 5A2 Line 2 — Fuel Pump assembly |

Why not: these are Pro-face LT3300 touch panels. Ignition has no native Pro-face driver. (TOP Server / Kepware does — which is why they work today.)

### 4c. 5G0 serialized cells — EtherNet/IP (2 devices) — CONFIRM

| Device | Line / station |
| --- | --- |
| 5G0_A1 | 5G0 Front — serialized assembly cell |
| 5G0_A2 | 5G0 Rear — serialized assembly cell |

Why “confirm”: catalogued as generic EtherNet/IP nodes. If these are Allen-Bradley (ControlLogix / CompactLogix / EtherNet-IP), Ignition’s native driver covers them and they move like the MicroLogix PLCs. We need the PLC make/model to confirm.

## 5. Options & recommendation

### Option A — Ignition only (remove both servers)

Move the Allen-Bradley PLCs to Ignition’s native drivers, and reimplement the scale protocol inside Ignition (raw TCP/serial driver + gateway scripting, including the pass/fail comparison). Pro-face works only if the LT3300 also exposes Modbus TCP.

- Pros: no third-party OPC licensing or support; single vendor (Ignition); one address space.

- Cons: the scale integration becomes custom software that Blue Ridge builds and maintains; the Pro-face cells are blocked unless they speak Modbus.

### Option B — Consolidate to a single OPC server (recommended)

Replace both TOP Server and OmniServer with one modern OPC server — KEPServerEX (PTC Kepware) — using its native drivers for the Allen-Bradley PLCs and Pro-face HMIs, plus its User-Configurable (U-CON) driver for the custom scale protocol (U-CON is the direct equivalent of OmniServer’s protocol builder). Ignition connects to it over OPC-UA.

- Pros: two servers become one; keeps native Pro-face support and the custom-scale capability without custom Ignition code; modern and well-supported.

- Cons: still one third-party OPC server (licensed).

- Note: TOP Server is itself built on Kepware technology, so this is not a large platform change — the real gain is collapsing two servers into one and absorbing the scales via U-CON, eliminating OmniServer.

### Recommendation

If the goal is fewer moving parts and better supportability, Option B (a single KEPServerEX with U-CON) is the pragmatic path — it removes OmniServer and the two-server split with the least custom development, and keeps every device on a supported driver. Option A (full Ignition-only) is achievable but trades a server license for scale-protocol code that Blue Ridge would then own; it is worth it only if removing all third-party OPC is a hard requirement and the scales prove simple.

## 6. What we need from MPP to finalize

| # | Device group | Information requested |
| --- | --- | --- |
| 1 | Weigh scales (7) | Make/model, connection type (RS-232 serial / Ethernet / serial-to-Ethernet converter), the data protocol, and whether the scale itself outputs a pass/fail or OmniServer computes it |
| 2 | Pro-face LT3300 (4) | Does the LT3300 expose Modbus TCP, or only the Pro-face protocol? |
| 3 | 5G0 cells (2) | PLC make/model for 5G0 Front and 5G0 Rear |

With these three answers we can size each option precisely and confirm whether “Ignition-only” is viable or a single-server consolidation is the right call.